## Contingency_Results
PROJECT: Regional Transmission Network Interconnection Study (N-1/N-2 Security Assessment)
CONFIDENTIAL & PROPRIETARY — SIMULATION DATASET EXCLUSIVE TO INTERNAL QA BENCHMARKING
Case | Element | Type | Nominal_kV | Voltage_pu | Loading_percent | Converged
N-0: Base Case Peak | BUS-400-01 (Slack) | Bus | 400 | 1.025 |  | Yes
N-0: Base Case Peak | BUS-220-02 (PV Gen) | Bus | 220 | 1.04 |  | Yes
N-0: Base Case Peak | BUS-220-03 (Load) | Bus | 220 | 0.975 |  | Yes
N-0: Base Case Peak | LINE-400/220-Tr1 | Transformer | 400 |  | 68.4 | Yes
N-0: Base Case Peak | LINE-220-01-04 | Line | 220 |  | 74.2 | Yes
N-0: Base Case Peak | BUS-132-05 (Sub) | Bus | 132 | 0.96 |  | Yes
N-1: Gen 2 Trip | BUS-220-02 (PV Gen) | Bus | 220 | 0.91 |  | Yes
N-1: Gen 2 Trip | BUS-132-05 (Sub) | Bus | 132 | 0.885 |  | Yes
N-1: Gen 2 Trip | LINE-220-03-06 | Line | 220 |  | 98.5 | Yes
N-1: Gen 2 Trip | LINE-132-05-08 | Line | 132 |  | 104.2 | Yes
N-1: Line 400-02 Outage | BUS-220-04 (Load) | Bus | 220 | 0.92 |  | Yes
N-1: Line 400-02 Outage | LINE-400-03-05 | Line | 400 |  | 114.5 | Yes
N-1: Line 400-02 Outage | TR-220/33-North | Transformer | 220 |  | 118 | Yes
N-1: Line 400-02 Outage | BUS-33-11 (Industrial) | Bus | 33 | 0.935 |  | Yes
N-1: Heavy Corridor Outage | BUS-132-09 (Load) | Bus | 132 | 0.86 |  | Yes
N-1: Heavy Corridor Outage | LINE-132-08-09 | Line | 132 |  | 126.5 | Yes
N-1: Heavy Corridor Outage | TR-132/33-East | Transformer | 132 |  | 122 | Yes
N-2: Dual Line Contingency | SYSTEM-WIDE | System | 400 |  |  | No
N-0: Base Case Off-Peak | BUS-400-01 (Slack) | Bus | 400 | 1.055 |  | Yes
N-0: Base Case Off-Peak | BUS-220-03 (Load) | Bus | 220 | 1.065 |  | Yes
N-0: Base Case Off-Peak | LINE-220-02-04 | Line | 220 |  | 45 | Yes